## Slide 1: The LHCb Experiment Control System:
On the path to full automation

## Slide 2: The Experiment Control System
Detector Channels
Front End Electronics
Readout Network
HLT Farm
Storage
L0
Experiment Control System
DAQ
DCS Devices (HV, LV, GAS, Cooling, etc.)
External Systems (LHC, Technical Services, Safety, etc)
TFC
Monitoring Farm
Is in charge of the Control and Monitoring of all areas of the experiment
Notes: In charge of the Control and Monitoring of:
  Data Acquisition System
    FE Electronics, Readout, Event Building, etc.
  Timing and Trigger Systems
    Timing & Fast Control (TFC)
    L0 Trigger
    High Level Trigger Farm
  Detector Control System
    Gas, High Voltages, Low Voltages, Temperatures...
  Experimental Infrastructure
    Cooling, Ventilation, Electricity distribution, ...
  Interaction with the outside world
    Magnet, Accelerator system, Safety system, etc.

## Slide 3: Homogeneity
Same architecture and same tools used throughout the Control System.
Generic Architecture:
LV Dev1
LV Dev2
LV DevN
DCS
SubDetN DCS
SubDet2 DCS
SubDet1 DCS
SubDet1 LV
SubDet1 TEMP
SubDet1 GAS
…
…
Commands
DAQ
SubDetN DAQ
SubDet2 DAQ
SubDet1 DAQ
SubDet1 FEE
SubDet1 RO
FEE Dev1
FEE Dev2
FEE DevN
Control Unit
Device Unit
…
…
Building Blocks:
INFR.
TFC
LHC
ECS
HLT
Status & Alarms

## Slide 4: The Control Framework
The JCOP* Framework is based on:
      SCADA System - PVSSII for:
        Device Description (Run-time Database)
        Device Access (OPC, Profibus, drivers) +DIM
        Alarm Handling (Generation, Filtering, Masking, etc)
        Archiving, Logging, Scripting, Trending
        User Interface Builder
        Alarm Display, Access Control, etc.
      SMI++ providing:
        Abstract behavior modeling (Finite State Machines)
        Automation & Error Recovery (Rule based system)
* – The Joint COntrols Project (between the 4 LHC exp. and the CERN Control Group)
Device Units
Control Units

## Slide 5: Device Units
Provide access to “real” devices:
  The FW provides interfaces to all necessary types of devices:
    LHCb devices: HV channels, Read Out boards, Trigger processes running in the HLT farm or Monitoring tasks for data quality, etc.
    External devices: the LHC, a gas system, etc.
  Each device is modeled as a Finite State Machine:
    It’s main interface to the outside world is a “State” and a (small) set of “Actions”.
Device Unit

## Slide 6: Hierarchical control
Each Control Unit:
  Is defined as one or more Finite State Machines
    It’s interface to outside is also a state and actions
  Can implement rules based on its children’s states
  In general it is able to:
    Include/Exclude children (Partitioning)
      Excluded nodes can run is stand-alone
    Implement specific behaviour & Take local decisions
      Sequence & Automate operations
      Recover errors
    User Interfacing
      Present information and receive commands
DCS
Muon DCS
Tracker DCS
…
Muon LV
Muon GAS
Control Unit

## Slide 7: FW – Graphical Editor
SMI++ Objects States & Actions
Parallelism, Synchronization
Asynchronous Rules

## Slide 8: Operation Domains
DCS Domain Equipment operation related to a running period (Ex: GAS, Cooling)
HV Domain Equipment operation related to the LHC State (Ex: High Voltages)
DAQ Domain Equipment operation related to a “RUN” (Ex: RO board, HLT process)
READY
STANDBY1
OFF
ERROR
Recover
STANDBY2
RAMPING_STANDBY1
RAMPING_STANDBY2
RAMPING_READY
NOT_READY
Go_STANDBY1
Go_STANDBY2
Go_READY
RUNNING
READY
NOT_READY
Start
Stop
ERROR
UNKNOWN
Configure
Reset
Recover
CONFIGURING
READY
OFF
ERROR
NOT_READY
Switch_ON
Switch_OFF
Recover
Switch_OFF
FSM templates distributed to all Sub-detectors
All Devices and Sub-Systems have been implemented using one of these templates

## Slide 9: ECS - Automation
Some Examples:
  HLT Control (~1500 PCs)
    Automatically excludes misbehaving PCs (within limits)
    Can (re)include PCs at run-time (they get automatically configured and started)
  RunControl
    Automatically detects and recovers SubDetector desynchronizations
    Can Reset SDs when problems detected by monitoring
  AutoPilot
    Knows how to start and keep a run going from any state.
  BigBrother
    Based on the LHC state:
      Controls SD Voltages
      VELO Closure
      RunControl

## Slide 10: Run Control
Matrix
Activity
Domain
X
Sub-Detector
Used for Configuring all Sub-Systems

## Slide 11: LHCb Operations
Two operators on shift:
  Data Manager
  Shift Leader has 2 views of the System:
    Run Control
    Big Brother
Big Brother
  Manages LHC dependencies:
    SubDetector Voltages
    VELO Closing
    Run Control

## Slide 12: ECS: Some numbers
DCS
SubDetN DCS
SubDet1 DCS
…
DAQ
SubDetN DAQ
SubDet1 DAQ
…
HV
TFC
LHC
HLT
ECS
Size of the Control Tree:
  Distributed over ~150 PCs
    ~100 Linux (50 for the HLT)
    ~ 50 Windows
  >2000 Control Units
  >50000 Device Units
Run Control Timing
  Cold Start to Running: 4 minutes
    Configure all Sub-detectors, Start & Configure ~40000 HLT processes (always done well before PHYSICS)
  Stop/Start Run: 6 seconds

## Slide 13: Conclusions
LHCb has designed and implemented a coherent and homogeneous control system
The Experiment Control System allows to:
  Configure, Monitor and Operate the Full Experiment
  Run any combination of sub-detectors in parallel in standalone
Some of its main features:
  Partitioning, Sequencing, Error recovery, Automation
  Come from the usage of SMI++ (integrated with PVSS)
LHCb operations now almost completely automated
  Operator task is easier (basically only confirmations)
  DAQ Efficiency improved to ~98%